St Louis Benchmark at Design Weather Conditions.

Analysis with (SEE) Energy Model

Last year’s analysis, several pages below, is for a ASHRAE Standard 90.1-2010 six-building campus with a six chiller/tower plant.

This year’s analysis will give the performance of a ASHRAE Standard 90.1-2010 large office building with a plant consisting of 3 chiller/towers, as defined by Table 2. Table 3 defines a Table 2 building with bad air control.

Also, the performance of a more efficient building with min reheat air handlers & efficient plant design is presented as defined by Table 4.

A system energy equilibrium (SEE) model is a tool for commissioning and evaluating the performance of a building and plant on any day. The purpose of this paper is to provide performance data on specify days so that building owners can judge the energy performance of their buildings against an ASHRAE Standard design, in this case a 90.1-20105 building and plant design.

Reader should review Anatomy of a Real Time Building Energy Model on this site.

Building 13 Story

Building=565,000 Ft-Sq

Building height=169 Ft

13 story building

Roof = 43,462 Ft-Sq

All walls 37.5% glass

Roof U=.048 Wall U=.090

Glass U=.55 Glass SHGC=.40

Footprint

South=240 Ft North=240 Ft

Each wall=40,560 Ft-Sq

East=181.09 Ft West=181.09 Ft

Each Wall=30,604 Ft-Sq

Figure 1: Building Description-Large Office Building Designed to Std. 90.1-20105

Figure 1 presents the modeled building of this study, a 565,000 square foot large office building based on the data provided by Liu5. The following analysis is for one building.

Figure 2: Top Chart-Design Day Weather-Bottom Chart5-Light kW, Plug kW, & # people

Figure 2 gives the lights and plug kW demand per time of day and the number of people in the building as interpreted from Liu5. Figures 1, 2 & Table 2 give sufficient data to (SEE) model the ASHRAE Standard 90.1-20105 building and plant.

Building Design

- Building 565,000 ft2. - No external solar shading. - Design weather-Figure 3. - Building design from Liu5. - Percent wall glass 37%. - Peak lights kW .81 watts/ft2. - Peak plugs kW .66 watts/ft2 - Return air to perimeter. - One VAV AHU/floor 24,000 CFM - Duct design 5.5 in. water - Fan powered terminals installed. - Return air fans installed. Building Control. - Lights on/off control 6% on after hours.. - Plugs on/off control 44% on after hours.. - Building pressure control, no infiltration. - Supply air = 55F - Supply water = 44F to 44.5F. - Stats control-no.. - Perimeter heat air temp-90F.. - VAV fan static control down to 1.5 in.. - Fresh air CFM control-yes.. - Fresh air heat stat set 42F.. Plant Design & Control - Chiller/Tower selection13.. Table 2: STD. 90.1-2010 Building.

| Chiller Design Load (Ton) | 324.0 |
| --- | --- |
| Chiller kW | 215.0 |
| Chiller kW/ton | .66 |
| Evap water flow rate (gpm) | 778.0 |
| Evap entering water temp (F) | 54.0 |
| Evap leaving water temp (F) | 44.0 |
| Evap refrigerant temp (F) | 38.8 |
| Evap refrigerant approach (F) | 5.2 |
| Evap pressure drop (ft. water) | 27.6 |
| Evap water velocity (ft. /sec.) | 10.6 |
| Cond heat rejection (ton) | 390 |
| Cond water flow rate (gpm) | 669 |
| Cond entering water temp (F) | 88 |
| Cond leaving water temp (F) | 102.0 |
| Cond refrigerant temp (F) | 106.9 |
| Cond refrigerant approach (F) | 4.9 |
| Cond pressure drop (ft. water) | 31.2 |
| Cond water velocity (ft. /sec) | 10.28 |
| Tower for (SEE) model | Tower15 |
| Design Wet bulb | 80.0F |
| Design Load | 390 ton |
| Tower water flow | 672 gpm |
| Approach temperature | 8.0 F |
| Calculated range | 14.00F |
| Range + approach | 22.00F |
| One cells with 15HP fan | 12 kW |
| Selected Tower15 | NC8402PAN1 |
| Cold water | 88F |
| Return water to tower | 102F |
| Capacity | 112% |
| Static lift | 10.6 ft. |
| Table 2 Chiller/Tower |  |

Table 2 gives the design parameters of the ASHRAE Standard 90.1-2010 building and plant as determined from Liu5.

Building Design with bad air control

- Building 565,000 ft2. - No external solar shading.. - Building design from Liu5. - Percent wall glass 37%. - Peak lights kW .81 watts/ft2. - Peak plugs kW .66 watts/ft2 - Return air to perimeter. - One VAV AHU/floor 24,000 CFM - Duct design 7.0 in. water - Fan powered terminals constant on. - Return air fans installed. Building Control. - Lights on/off control 6% on after hours.. - Plugs on/off control 44% on after hours.. - Building air infiltration, .1cfm/wall ft2. - Supply air = 55F - Supply water = 44F to 44.5F. - Stats control-no.. - Perimeter heat air temp-90F.. - VAV fan static control-down to 5.0 in.. - Fresh air CFM control-yes.. - Fresh air heat stat set 75F.. Plant Design & Control - Chiller/Tower selection13.. Table 3: Table 2 with Bad Control.

Table 3 is the Table 2 ASHRAE Standard 90.1-2010 design with bad air side control. These rather minor bad control of the air side will have a significant impact on the energy consumption of the building and plant. The point: control is a key to minimizing the energy consumption of a building and plant.

SEE MODEL DESIGN

Table 4 defines the design of the efficient design building with min reheat air handlers & efficient plant design.

Building Design

- Building 565,000 ft2. - No external solar shading. - Design weather-Figure 3. - Building design from SEE Model. - Percent wall glass 37%. - Peak lights kW .81 watts/ft2. - Peak plugs kW .66 watts/ft2 - Return air to perimeter. - Min reheat AHU’s installed - Duct design 5.5 in. water - Fan powered terminals removed. - Return air fans removed. Building Control. - Lights on/off control 6% on after hours.. - Plugs on/off control 44% on after hours.. - Building pressure control, no infiltration. - Supply air = 55F - Supply water = 44F to 44.5F. - Stats control-yes.. - Perimeter heat air temp-100F.. - VAV fan static control-yes down to1.5 in.. - Fresh air CFM control-yes.. - Fresh air heat stat set 42F.. Plant Design & Control - Chiller/Tower selection4.. Table 4: SEE Model Building.

Comparing Table 2 and Table 4 illustrates five differences. The fan power terminals and return fans are removed in Table 4. The stats are controlled, the perimeter heat air is 100F verses 90F for Table 2 System and min reheat AHUs are installed.

| Chiller Design Load (Ton) | 300.0 |
| --- | --- |
| Chiller kW | 168.0 |
| Chiller kW/ton | .56 |
| Evap water flow rate (gpm) | 514.0 |
| Evap entering water temp (F) | 58.0 |
| Evap leaving water temp (F) | 44.0 |
| Evap refrigerant temp (F) | 40.8 |
| Evap refrigerant approach (F) | 3.2 |
| Evap pressure drop (ft. water) | 16.4 |
| Evap water velocity (ft. /sec.) | 6.92 |
| Cond heat rejection (ton) | 353 |
| Cond water flow rate (gpm) | 850 |
| Cond entering water temp (F) | 85. |
| Cond leaving water temp (F) | 95. |
| Cond refrigerant temp (F) | 98.6 |
| Cond refrigerant approach (F) | 3.6 |
| Cond pressure drop (ft. water) | 21.7 |
| Cond water velocity (ft. /sec) | 8.25 |
| Tower for (SEE) model | Tower15 |
| Design Wet bulb | 80.0F |
| Design Load | 353 ton |
| Tower water flow | 850 gpm |
| Approach temperature | 5.0 F |
| Calculated range | 10.00F |
| Range + approach | 15.00F |
| One cells with 15HP fan | 16 kW |
| Selected Tower15 | NC8403QLN1 |
| Cold water | 85F |
| Return water to tower | 95F |
| Capacity | 106.7% |
| Static lift | 12.2 ft. |
| Table 4 SEE Model Chiller/Tower |  |

The Table 4 chiller/Tower design is changed from Table 2 as illustrated by the Table 4 above. This chiller selection is not the most efficient in terms of chiller kW/ton but is the most efficient in terms of plant kW/ton. The point: chiller kW/ton is not the issue, plant kW/ton is.

Figure 3: Design Weather

Figure 3 gives the assumed design weather. Each of the designs, Table 2, 3 , & 4 will be evaluated with the SEE Model.

The charts at left give the hourly watts/ft2 for the three designs plus the sum for the day, illustrating the significant increase with the Table 3 design and significant decrease with the Table 4 design. The above chart gives day sums for components of the system.

The chart at left gives the building 24-hour energy balance and the above chart gives the plant 24-hour energy balance.

The above chart gives the 24-hour building energy balance with plant load defined.

The above chart is the 24-hour energy balance of the total system giving the energy out at the tower.

The SEE Model can give an energy balance for any hour.

The above chart gives the building energy balance (EB) at 4PM in terms of btu/ft2.

The above chart gives the building EB with fewer components and in (ton). If building kW and plant load were measured values, this EB would be easy to work with and balance the building weather term.

The above plant EB would be easy to verify if the plant load and/or tower energy out was metered.

The above chart gives 4PM building or plant load EB with more detail, illustrating the complexity and value of the SEE Model energy balance.

The above chart illustrates the detail the SEE Model can provide. The chart suggests that adequate ventilation occurs during occupied hours.

The above chart gives plant performance illustrating the advantage of the Table 4 design.

This above analysis is at design weather conditions. We will now look at real weather performance.

St Louis Benchmark at Real Weather Conditions of March 11, 2022.

Analysis with (SEE) Energy Model

Last year’s analysis, several pages below, is for a ASHRAE Standard 90.1-2010 six-building campus with a six chiller/tower plant.

This year’s analysis will give the performance of a ASHRAE Standard 90.1-2010 large office building with a plant consisting of three chiller/towers, as defined by Table 2 above.

Also, the performance of a more efficient building with min reheat air handlers & efficient plant design is presented defined by Table 4 above.

This real weather analysis will also include the performance of the Table 2 system with bad air control, Table 3 illustrates the bad control of the Table 2 design.

These bad control features of Table 3 result in significant increase in energy consumption at cold weather conditions as demonstrated by the following.

Weather and occupancy profile

The above figure gives the weather data for this day, top chart. The bottom chart is repeated from above.

The figure at right illustrates that the Table 3 system with bad air control, top chart, consumes significantly more energy than the Table 2 system, middle chart, a properly controlled ASHRAE Standard 90.1-2010 large office building. The bottom chart, Table 4 system, consumes significantly less than the Table 2 system. Note that the building watts/ft2 includes lights, plug, and air handler use and does not include heat and the plant energy use.

The total energy use of each system is building watts/ft2 + heat watts/ft2 + plant watts/ft2.

The figure at left gives the total energy consumption for this day for components of the system. Clearly what seems like rather insignificant bad control can have a big effect on cold days.

If only one meter exists on a building, then the real building watts/ft2 could be used to judge an existing building with weather like this day.

The Table 4 design is clearly the best performer.

The reader can judge the performance of a real building on a similar day by comparing performance to these figures. If the 24-hour energy consumption of a large office falls close to the center figure at left, then the building is operating close to 90.1-2010 performance as defined by Table 2. Values that approach the top chart, Table 3, are out of control. The bottom chart illustrates what is possible by designing an office building to Table 4.

The SEE Model provides an enormous amount of data that can be reviewed at Nelson4. The Energy Balance analysis is a feature of the SEE Model that provides an ability to evaluate the performance of a real building on any day.

Next, we look at Energy Balance charts for the weather day defined above.

Energy Balance analysis is a major feature of the SEE Model. The above figure gives the 24-hour plant load energy balance.

The above figure gives the 24-hour plant energy balance.

The above figure gives the 24-hour sum plant load energy balance.

The above figure gives the total 24-hour system energy balance, energy out at the tower.

The above figure gives the 24-hour sum for the plant energy balance.

The above figure gives the plant load energy balance at 4PM. An energy balance can be given, by the SEE Model, for any hour.

The above figure is a simpler energy balance in (ton) load. Building kW and plant load could be metered values, therefore providing a method to check and correct the other values.

The above figure is the plant energy balance in (ton) load. The only value that cannot be directly metered is the pump heat out and it could be closely estimated by knowing pump kW.

The above figure gives a greater detail plant energy balance in (ton) load.

The above figures have demonstrated the energy balance features of the SEE Model. The SEE Model can give charts of any variable of the building and plant and can also give schematics for any hour. The schematics, as given above are very valuable in understanding how the varies components of a building or plant act under given conditions and illustrates Ein = Eout as occurs in a real building and plant.

The following two sets of charts deal with ventilation and plant performance.

The above chart illustrates that Table 4 design demands significantly less fan kW. All three designs appear to have adequate perimeter supply air with the top chart showing the Table 3 design with high values of perimeter CFM.

The above charts show the Table 4 design demands less chiller kW. Note the number of chiller/towers on to meet the load of each design.

SUMMARY Performance of Table 3, Table 2, & Table 4 on March 11, 2022.

These charts and Tables 2, 3, & 4 above give information and data that the reader can use to judge office buildings in St Louis Mo. on similar weather days.

These two charts are copied from above.

March 11, 2022, weather

The above chart gives the weather for this day and the chart at right gives the kW performance of each design. On a day with weather close to above a ASHRAE Standard design would perform like the middle chart at right. An office building that approaches the values of the top chart is out of control. The bottom chart gives what is possible with efficient design. Tables 2, 3, and 4 above define each design.

St Louis Benchmark at Real Weather Conditions of March 14, 2022.

Weather for March 14, 2022

The weather significantly changes from March 11 to March 14 and so does the energy use of the three designs as shown at right. Comparing the March 11 charts above with the charts at right illustrates a big reduction in energy consumption on March 14. The middle chart gives the SEE model result of a 90.1-2010 design and the top chart is with bad air side control. The bottom charts give an efficient design. The three designs are defined by above Tables 2, 3, and 4.

Stay tuned for more weather days.

Energy performance of Three Designs

St Louis MO.-(SEE) Model Building Energy Benchmark at Real Weather Conditions.

Introduction/Building Description

A system energy equilibrium (SEE) model is a tool for commissioning and evaluating the performance of a building and plant on any day. The (SEE) model also provides the capability to judge the performance of systems on any day. The purpose of this paper is to provide performance data on specify days so that building owners can judge the energy performance of their buildings against an ASHRAE Standard design, in this case a 90.1-20105 building and plant design.

Reader should review Anatomy of a Real Time Building Energy Model on this site.

Building 13 Story

Each Building=565,000 Ft-Sq

Building height=169 Ft

13 story building

Roof = 43,462 Ft-Sq

All walls 37.5% glass

Roof U=.048 Wall U=.090

Glass U=.55 Glass SHGC=.40

Footprint

South=240 Ft North=240 Ft

Each wall=40,560 Ft-Sq

East=181.09 Ft West=181.09 Ft

Each Wall=30,604 Ft-Sq

Figure 1: Building Description Large Office Building Designed to Std. 90.1-20105

Figure 1 presents the modeled building of this study, a 565,000 square foot large office building based on the data provided by Liu5. The office campus is assumed to consist of six Figure 1 buildings.

Figure 2 top chart gives the assumed design day weather conditions. The secondary horizontal axis of gives the design day percent clear sky.

Figure 2: Top Chart-Design Day Weather-Bottom Chart5-Light kW, Plug kW, & # people

Figure 2 bottom chart gives the lights and plug kW demand per time of day and the number of people in the building as interpreted from Liu5. Figures 1 & 2 plus Table 2 give sufficient data to (SEE) model the ASHRAE Standard 90.1-20105 building and plant.

Building Location and Design

- Location=Kansas City Mo. - Building 565,000 ft2. - No external solar shading. - Design weather-Figure 2. - Building design from Liu5. - Percent wall glass 37%. - Peak lights kW .81 watts/ft2. - Peak plugs kW .66 watts/ft2 - Return air to perimeter-no change. - One VAV AHU/floor 26,400 CFM - Duct design 7.0 in. water - Fan powered terminals installed. - Return air fans installed. Building Control. - Lights on/off control 6% on after hours.. - Plugs on/off control 44% on after hours.. - Building pressure control, no infiltration. - Supply air = 55F - Supply water = 44F to 44.5F. - Stats control-yes.. - Perimeter heat air temp-105F.. - VAV fan static control-yes.. - Fresh air CFM control-yes.. - Fresh air heat stat set 42F.. Plant Design & Control - Chiller/Tower selection13.. Table 2: System.

Table 2 gives the building and plant design defined here as an efficient design and the as constructed system.

Figure 3: Watts/ft2 Design Day Weather

Figure 3 gives the watts/ft2 performance of the Figures 1, 2 and Table 2 building and plant, defined here as the ASHRAE Standard 90.1-20105 design, also defined here as the “Table 2 system”.

The total 24-hour consumption operating at the design weather conditions of Figure 2 is 41.487 watts/ft2. The building not including heat is 28.500 watts/ft2 and the plant is 12.99 watts/ft2. These values can be used to judge office buildings when operating close to design weather of this city.

Specific days of weather will be addressed below showing performance of the Table 2 system and the Table 3 system defined below as the Table 2 system with poor control.

Energy Balance of Table 2 System

Figure 4: Table 2 System Energy Balance at Design conditions at 4PM of Figure 2

Figure 4 would have been determined during the design of this building and plant. Figure 5 gives the 24-hour energy balance data in (btu/ft2) so that data for any building can be judged against this (SEE) model Standard 90.1-2010 building5 as defined by Table 2.

Figure 5 gives the 24-hour energy balance of the plant load and the energy out at the tower.

Figure 5: Table 2 System 24 Hour Energy Balance Top chart plant energy balance, Bottom chart system energy balance.

Chiller/Tower Design Data

Tables 1 gives (SEE) model input design data for the chiller and tower and Table 1A defines the chiller/tower design lift. The chiller/tower has 1,000-ton capacity at design conditions of 101F dry bulb and 78F wet bulb. The chiller evaporator is selected with a 2.6F refrigerant approach and the condenser is 1.6F refrigerant approach.

The tower is selected15 at 1,173-ton load and 78F wet bulb with an approach to wet bulb of 8F and flow of 2,000 gpm with a calculated range of 14.13F. The tower is a one cell unit with a 50hp fan.  Condenser design leaving water temperature is 100.13F and tower leaving water is 86F.

| Chiller Design Load (Ton) | 1000.0 |
| --- | --- |
| Chiller kW | 583.0 |
| Chiller kW/ton | .583 |
| Evap water flow rate (gpm) | 1500.0 |
| Evap entering water temp (F) | 60.0 |
| Evap leaving water temp (F) | 44.0 |
| Evap refrigerant temp (F) | 41.4 |
| Evap refrigerant approach (F) | 2.6 |
| Evap pressure drop (ft. water) | 34.5 |
| Evap water velocity (ft. /sec.) | 8.38 |
| Cond heat rejection (ton) | 1173 |
| Cond water flow rate (gpm) | 2000 |
| Cond entering water temp (F) | 86 |
| Cond leaving water temp (F) | 100.13 |
| Cond refrigerant temp (F) | 101.73 |
| Cond refrigerant approach (F) | 1.6 |
| Cond pressure drop (ft. water) | 43 |
| Cond water velocity (ft. /sec) | 9.71 |
| Tower for (SEE) model | Tower15 |
| Design Wet bulb | 78.0F |
| Design Load | 1173 ton |
| Tower water flow | 2000 gpm |
| Approach temperature | 8.0 F |
| Calculated range | 14.13F |
| Range + approach | 22.13F |
| One cells with 50HP fan | 40 kW |
| Selected Tower15 | NC8409UAN1 |
| Cold water | 86F |
| Return water to tower | 100.13F |
| Capacity | 104.4% |
| Static lift | 12 ft. |

Table 1: Chiller/Tower Design Data

Chiller/Tower Lift

Chiller lift20 equals condenser refrigerant temperature minus evaporator refrigerant temperature as defined by Table 1A for this chiller/tower selection. Table 1A illustrates the design values that define the refrigerant temperatures and therefore chiller lift. All values are taken from Tables 1. The condenser refrigerant temperature is the sum of wet bulb + tower approach = entering condenser water + tower range = leaving condenser water + condenser refrigerant approach = 101.73F refrigerant temperature. The evaporator refrigerant temperature is determined by the design values of Table 1. Evaporator entering water minus evaporator delta T equals leaving chiller water temperature minus evaporator refrigerant approach temperature equals evaporator refrigerant temperature. The evaporator refrigerant temperature can also be determined by simply subtracting the evaporator refrigerant approach temperature from the evaporator supply water temperature, (44F – 2.6F = 41.4F). Therefore, chiller lift = 101.73F – 41.4F = 60.33F. Chilled water supply temperature has a significant effect on chiller lift and therefore chiller kW demand.

| Design Chiller Lift (F) |  |
| --- | --- |
| Condenser refrigerant | 101.73F |
| Condenser refrigerant approach | 1.6F |
| Leaving condenser water | 100.13F |
| Tower range | 14.13F |
| Entering condenser water | 86F |
| Tower approach | 8.0F |
| Wet bulb temperature | 78.0F |
| Chiller lift = 101.73F – 41.4F = 60.33F |  |
| Evaporator entering water | 60F |
| Evaporator delta temperature | 16F |
| Leaving chilled water temperature | 44F |
| Evaporator refrigerant approach | 2.6F |
| Evaporator refrigerant temperature | 41.4F |

Table 1A: Chiller/Tower Lift-Design Conditions

Table 1 & 1A are chiller/tower design selection values for a Kansas City Missouri plant. Operating at the design conditions of this city is illustrated by the plant schematic. Detail plant design/selection is a (SEE) plant model capability that will be presented at, “System Energy Equilibrium (SEE) Building Energy Model Development & Verification”. http://kirbynelsonpe.com/

Table 2 Plant Schematic-Design Load

The Table 2 Plant Schematic illustrates the lift at design weather is 57.5F verses 60.33 of Table 1A. Nomenclature is given below so the reader can study the plant schematic.

(EUI) Estimates (kbtu/ft2-yr) for the

Table 2 System

Figure 6: Table 2 System (EUI) estimate & System Components (EUI) per season

Figure 6 is an estimate of annual (EUI) for the Table 2 system and Figure 7 is for the Table 3 system. The bottom charts of Figures 6 & 7 give the (EUI) values of the system components at the four seasons. The Table 3 system is the Table 2 system with poor control. Poor control of the Table 2 system more than doubled the (EUI) value of the Table 2 system.

Table 3 System-Poor Control

Each of the building controls listed by Table 2 are changed with Table 3 except the 55F supply air temperature and the plant control. The (SEE) model can evaluate each of these poor control issues, and others, as standalone or as additive effect on the performance of the system.

System aging can also have a significant effect on the performance of a system but will not be addressed here, perhaps later.

Building Location and Design

- Location=Kansas City Mo. - Building 565,000 ft2. - No external solar shading. - Average ambient temperatures - Percent clear sky s defined below.. - Building design per Liu5. - Percent wall glass 37%. - Peak lights kW .81 watts/ft2. - Peak plugs kW .66 watts/ft2 - Return air to perimeter-no change. - One VAV AHU/floor 26,400 CFM - Duct design 5.5 to 7.0 in. water - Fan powered terminals installed - Return air fans installed Building Control. - Lights on/off control from 6% on after hours to 67% on.. - Plugs on/off control 44% on after hours to 67% on.. - Building pressure control; infiltration of .2 cfm/ft2 walls max-varies as AHU cfm. - Supply air = 55F - Supply water = 44F to 44.5F. - Stats control-NO.. - Perimeter heat air temp-90F.. - VAV fan static control-NO.. - Fresh air CFM control-NO.. - Fresh air heat stat set from 42F to 60F.. Plant Design & Control - Chiller/Tower selection13.. Table 3: System-Poor Control.

The (EUI) estimates of Figure 6 & 7 are at average weather for the four seasons with 80% clear sky for summer, 60% clear sky for spring and fall, and 20% clear sky for winter weather.

Figures 6 & 7 provide estimated annual (EUI) values so the annual performance of a real building and plant can be judged. Below will provide performance on specific days for Energy Balance Analysis. See Anatomy of a Real Time Building Energy Model for analysis procedures.

Figure 7: Table 3 System (EUI) estimate & System Components (EUI) per season

An office building or campus for this city should have an annual (EUI) close to Figure 6. If the annual (EUI) is greater than Figure 6 then a (SEE) model analysis of the building might be in order. This site4 will provide an approach to energy balance analysis with (SEE) model.

This completes the introduction that give the performance of the Table 2 & 3 systems at design day conditions. The remaining sections of this paper will give performance of the Table 2 & 3 systems at real weather.  Nomenclature is given at the end.

Suggest reader visit; Anatomy of a Real Time Building Energy Model on this site that gives (SEE) model analysis procedures.

Stay tuned for more real weather days to be Benchmarked.

Best Regards to All

Kirby Nelson P.E.

Life Member ASHRAE

References

- Introduction to Thermodynamics and Heat Transfer. 1956 Prentice-Hall, Inc. by David A. Mooney.

- Thermal Environmental Engineering third edition. 1998 Prentice-Hall Inc. by Thomas H. Kuehn, chapter 3.

- ASHRAE Journal May 2016. “Modeled Performance Isn’t Actual Performance”

- Nelson, Kirby. “System Energy Equilibrium (SEE) Building Energy Model Development & Verification”. http://kirbynelsonpe.com/

- Liu, B. May 2011. “Achieving the 30% Goal: (copy and paste) https://www.energycodes.gov/sites/default/files/documents/BECP_Energy_Cost_Savings_STD2010_May2011_v00.pdf

- Real weather data www.wunderground.com/

- Nelson, K. “7 Upgrades to, Reduce Building Electrical Demand” ASHRAE Journal, December, 2006,

- Nelson, K. “Simulation Modeling of a Central Chiller Plant” CH-12-002. ASHRAE 2012 Chicago Winter Transactions.

- Nelson, K. “Simulation Modeling of Central Chilled Water System” CH-12-003. ASHRAE 2012 Chicago Winter Transactions.

- Kavanaugh, S. “Fan Demand and Energy” ASHRAE Journal, 2000.

- Faris, Gus “Fan-Powered VAV Terminal Units” ASHRAE Journal November 2017

- Kettler, John “Return Fans or Relief Fans” ASHRAE Journal April 2004.

- Taylor, S. 2011. “Optimizing design & control of chiller plants.” ASHRAE Journal (12).

- Nelson, Kirby “The System Energy Equilibrium Model for Chiller Plants, Part 1” Engineered Systems, July 2020.

- Marley Tower SPX Cooling Technologies UPDATE Version 5.4.2

- Steven Taylor. ASHRAE Journal June 2007. “VAV System Static Pressure Setpoint Reset.”

- Carrier System Design Manual

- Miles Ryan. ASHRAE Journal February 2021. “Understanding Cascade Control and Its Applications For HVAC”

- Schwedler, Mick. July 1998 “Take It to The Limit…Or Just Halfway?” ASHRAE Journal.

- 2020 ASHRAE HANDBOOK, HVAC Systems and Equipment, page 43.10 Figure 11 Temperature Relations in a Typical Centrifugal Liquid Chiller.

Real Weather Performance of Table 2 & Table 3 Systems

The following will give (SEE) model results at real weather conditions so that building owners can judge their buildings against ASHRAE Standard 90.1-2010 design. Values close to Table 2 values suggests a building that is operating close to ideal performance. Values close to Table 3 values suggests a building that is out of energy control.

Spring April 30, 2021

Figure A: Real Weather

Figure A illustrates the real weather6 for this day.

Figure B top chart gives a 24-hour total watts/ft2 for the Table 2 system that is much less than the Table 3 system, bottom chart.

If the real system falls close to the Table 2 system 24-hour values, then the real system is probably operating efficiently on this date. However, the system should be checked at other weather conditions and different seasons.

Figure B: 24 Hour Performance-Table 2&3 Systems

A system that has values on this day that are close to the Table 3 system, bottom chart of Figure B, is operating far outside of efficient performance. Suggest the reader visit; Anatomy of a Real Time Building Energy Model on this site that gives (SEE) model analysis procedures.

Stay tuned in for more real weather days.

NOMENCLATURE                                                               Each of the more than 200 variables are defined.

Building structure.

BLD ft2 = air-conditioned space

# Floors = number of building floors

Roof ft2 = roof square feet

N/S wall ft2 =north/south wall square feet

E/W wall ft2 =east/west wall square feet

Wall % glass = percent of each wall that is glass

Glass U = glass heat transfer coefficient

Wall U = wall heat transfer coefficient

Glass SHGC = glass solar heat gain coefficient

Wall emit = wall solar index

Building interior space;

Rooftrans-ton =transmission through roof (ton)

Roofsky-lite-ton =sky lite load (ton)

Peopleton sen&lat = sensible & latent cooling load due to people (ton)

Plugton&kW = cooling load & kW due to plug loads

Lightton&kW = cooling load & kW due to lights

Total Bldint-ton = total building interior load (ton)

(int-cfm) to-per-return = CFM of interior supply air that returns to perimeter of building

Tstat-int = interior stat set temperature (F)

Bldint-air-ton = supply air ton to offset interior load

BLD kW = total building kW demand

FAN kW = total fan kW

HEAT kW = total kW due to heat

SITE kW = total site kW=Bld+ Fan+Heat

Building perimeter space;

%clear sky = percent clear sky

Tdry bulb = outside dry bulb temperature (F)

Twet bulb = outside wet bulb temperature (F)

Ex/Infillat-ton = latent air infiltration or exfiltration (ton)

Ex/InfilCFM = air infiltration or exfiltration CFM

Exfilsen-ton =sensible air exfiltration or infiltration (ton)

Walln trans ton = north wall transmission (ton)

Walls trans ton = south wall transmission (ton)

WallE trans ton  = east wall transmission (ton)

Wallw trans ton = west wall transmission (ton)

Walltot-trans-ton = total wall transmission (ton)

GlassN-trans-ton = north wall glass transmission (ton)

GlassS-trans-ton = south wall glass transmission (ton)

GlassE-trans-ton = east wall glass transmission (ton)

GlassW trans-ton = west wall glass transmission (ton)

Glasstot-trans-ton = total transmission thru glass (ton)

GlassN-solar-ton = north glass solar load (ton)

GlassS-solar-ton = south glass solar load (ton)

GlassE-solar-ton = east glass solar load (ton)

GlassW-solar-ton = west glass solar load (ton)

Glasstot-solar-ton = total glass solar load (ton)

(int cfm)per-ton = effect of interior CFM to wall (ton)

Total Bldper-sen-ton total perimeter sensible load (ton)

Tstat-per = perimeter stat set temperature (F)

Bldper-air-ton = supply air ton to offset perimeter load

Air handler duct system-Interior duct

Tair supply int = temp air supply to building interior (F)

(fan)int ter ton&kW = interior ton & kW due to terminal fans

(D)int-air-ton = cooling (ton) to building interior duct

Tair coils = supply air temperature off coils to duct (F)

(D)int-CFM = supply air CFM to building interior duct

Perimeter duct

Tair supply per =temp (F) air supply to building perimeter

(fan)per ter ton&kW = perimeter ton & kW of terminal fans

Theat-air = temp supply air before terminal fan heat (F)

(D)heat-ton&kW = heat to perimeter supply air ton & kW

Treheat air = temp perimeter supply air after reheat (F)

(D)reheat ton&kW = reheat of perimeter supply air ton & kW

(D)per-air-ton = cooling (ton) to perimeter duct

Tair coils = supply air temperature off coils to duct (F)

(D)per-CFM = supply air CFM to perimeter duct

Coil

(Coil)sen-ton = sensible load on all coils (ton)

(Coil)cap-ton = LMTD * UA = capacity (ton) one coil

LMTD = Coil log mean temperature difference (F)

(Coil)L+s-ton = latent + sensible load on all coils (ton) transferred to Plant

UA = coil heat transfer coefficient * coil area. UA varies as a function water velocity   (coil)gpm thru the coil, as the (coil)gpm decreases the coil capacity decreases.

(one Coil)ton = load (ton) on one coil

VAV Fan system

Fresh air

statFA = fresh air freeze stat set temperature (F)

TFA to VAV = temperature of fresh air to VAV fan

(FA)sen-ton = fresh air sensible load (ton)

(FA)CFM = CFM fresh air to VAV fan inlet

(FA)Lat-ton = fresh air latent load (ton)

(FA)kW = heat kW to statFA set temperature

Air return

TBLD-AR = return air temp (F) before return fans

(Air)ret-CFM = CFM air return from building

(FAN)ret-kW = return fans total kW

(FAN)ret-ton = cooling load (ton) due to (FAN)ret-kW

(Air)ret-ton = return air (ton) before return fans

TAR to VAV = TBLD-AR + delta T due to return fans kW

VAVret-sen ton = return sensible (ton) to VAV fans inlet

VAVret-lat ton = return latent (ton) to VAV fans inlet

VAVret-CFM = return CFM to VAV fans inlet

Exhaust air

ExLat-ton = latent load (ton) exhausted

ExCFM = CFM of exhaust air

TEx = temperature of exhaust air

Exsen-ton = sensible load (ton) exhausted

VAV Fans

Tret+FA = return and fresh air mix temperature (F)

(dh) = VAV air static pressure (in)

Efan-VSD = VAV fans efficiency

VAVinlet-sen-ton = sensible load (ton) inlet to VAV fans

VAVinlet-lat-ton = latent load (ton) inlet to VAV fans

Tair-VAV = temp air to coils after VAV fan heat

(FAN)VAV-CFM = CFM air thru coils

(FAN)ton-VAV = load (ton) due to VAV fan kW

(FAN)kW-VAV = total VAV fan kW demand

AIR SIDE SYSTEM PLUS BUILDING

FAN kW = total air handlers kW

SITE kW = total site or air side kW

Plantton = (COIL)L+s ton load (ton) to plant

CENTRAL PLANT

# Buildings = number of buildings served by plant

Plant ton = total load (ton) to plant

Primary/secondary pumping nomenclature

gpmevap = total gpm flow thru one evaporators

(H)pri-total = total primary pump head (ft) = (H)pri-pipe + (H)pri-fittings + (H)pri-bp + (H)evap

(H)pri-pipe = primary pump head due to piping (ft)

(H)pri-fittings = primary head due to pump & fitting (ft)

(Ef)c-pump = efficiency of chiller pump

Pc-heat-ton = chiller pump heat to atmosphere (ton)

Pc-kW = one chiller pump kW demand (kW)

Pchiller-# = number chiller pumps operating

(lwt)evap = temperature water leaving evaporator (F)

Tbp = temperature of water in bypass (F)

gpmbp = gpm water flow in bypass

(H)pri-bp = head if chiller pump flow in bypass (ft)

(ewt)evap = temp water entering evaporator (F)

Psec-heat-ton = secondary pump heat to atmosphere (ton)

Psec-kW = kW demand of secondary pumps

Efdes-sec-p = design efficiency of secondary pumping

Efsec-pump = efficiency of secondary pumping

(H)sec = secondary pump head (ft) = (H)sec-pipe + (H)sec-bp + (H)coil + (H)valve

(H)sec-pipe = secondary pump head due to pipe (ft)

(H)sec-bp = head in bypass if gpmsec > gpmevap

GPMsec = water gpm flow in secondary loop

(ewt)coil = water temperature entering coil (F)

Pipesize-in = secondary pipe size (inches)

(lwt)coil = temperature of water leaving coil (F)

Evaporator

(evap)ton = load (ton) on one evaporator

TER = evaporator refrigerant temp (F)

TER-app = evaporator refrigerant approach (F)

EVAPton = total evaporator loads (ton)

(H)evap = pump head thru evaporator (ft)

(evap)ft/sec = velocity water flow thru evaporator

(evap)des-ft/sec = evaporator design flow velocity

Compressor:

(chiller)kW = each chiller kW demand

(chiller)lift = (TCR – TER) = chiller lift (F)

(chiller)% = percent chiller motor is loaded

(chiller)# = number chillers operating

(CHILLER)kW = total plant chiller kW

(chiller)kW/ton = chiller kW per evaporator ton

Plant kW = total kW demand of plant

(Plant)kW/site ton = Plant kW per site ton

Condenser nomenclature:

(cond)ton = load (ton) on one condenser

TCR = temperature of condenser refrigerant (F)

TCR-app = refrigerant approach temperature (F)

(COND)ton = total load (ton) on all condensers

(H)cond = tower pump head thru condenser (ft)

(cond)ft/sec = tower water flow thru condenser

Tower piping nomenclature

Pipesize-in = tower pipe size (inches)

gpmT = each tower water flow (gpm)

GPMT = total tower water flow (gpm)

(H)T-total = total tower pump head (ft)

PT-heat = pump heat to atmosphere (ton)

PT-kW = each tower pump kW demand

EfT-pump = tower pump efficiency

Ptower # = number of tower pumps

(H)T-pipe = total tower pump head (ft)

(ewt)T = tower entering water temperature (F)

(H)T-static = tower height static head (ft)

Trange = tower range (F)= (ewt)T – (lwt)T

(lwt)T = tower leaving water temperature (F)

Tapproach =  (lwt)T – (Twet-bulb)

Tower nomenclature

tfan-kW = kW demand of one tower fan

Tfan-kW = tower fan kW of fans on

tfan-%  = percent tower fan speed

tton-ex = ton exhaust by one tower

T# = number of towers on

Tton-ex = ton exhaust by all towers on

Trg+app = tower range + approach (F)

One hour performance indices

BLDkW = kW demand of building lights & plug loads

FankW = air side fans kW, VAV, return terminals

Ductheat = perimeter heat to air supply

FAheat = heat added to fresh air

Heattotal = total heat added to air

PlantkW = total plant kW

SystkW = total system kW

CCWSkW = air side system + plant kW

ChillerkW/evap ton = chiller kW/evaporator ton performance

PlantkW/site ton = plant kW per site or air side ton

CCWSkW/site ton = CCWS kW per load to plant

WeatherEin-ton = weather energy into the system

SitekW-Ein-ton = load (ton) due to site kW

PlantkW-Ein-ton = load (ton) due to plant kW

TotalEin-ton = total energy in to system (ton

Pumptot-heat-ton = total pump heat out (ton)

AHU Exlat ton = air exhausted latent ton

AHU Exsen ton = air exhausted sensible ton

Tower Tton Ex = energy exhausted by tower (ton)

Total Eout ton = total energy out of system (ton)

24 hour performance indices

BLD24hr-kW = building 24 hour kW usage

Fan24hr-kW = fan system 24 hour kW usage

Duct24hr-heat kW or therm = duct heat

FA24hr heat kW or therm = fresh air heat

Heat24hr total kW or therm = total heat into system

Plant24hr kW = plant 24 hour kW usage

Syst24hr kW & therm = total system 24 hour energy usage

Peoplesen+lat ton =total load (ton) due to people

Enfil24hr cfm energy = change in internal energy

Weather24hr-Ein-ton = 24 hour weather energy into system

SITE24hr-kW-Ein-ton = 24 hour energy into site

Plant24hr-kW-Ein-ton = 24 hour kW energy into plant

Total24hr-Ein-ton = total 24 hour energy into system

Pump24hr Heat out-ton = pump heat to atmosphere (ton)

AHU Ex24hr Lat ton = exhausted latent load from building

AHU Ex24hr-sen-ton = exhausted sensible load from bl