Paris France Benchmark Data for May 20, 2022

This analysis is performed with a System Energy Equilibrium (SEE) Model.

Go to the April 2022 ASHRAE Journal Newsletter to see a review of the SEE Model.

A few pages below are design data for the two systems analyzed, a 90.1-2010 large office building and the same building with revised air handling system and a low lift refrigerant design plant. This section will present real weather performance of the two systems.

Weather on this day

The above chart gives the weather data that is input to the SEE Model to define the energy consumption for this day’s weather, day benchmark data, of the two designs on this 24-hour day.

Why do this?

The purpose of day benchmarking is the give engineers a tool to show building owners opportunities to reduce energy consumption, and therefore cost, in their building. The result will be less kW demand on the energy grid of a community and the generation of business to accomplish the energy reductions. A win-win for the community, create business and reduce power requirements.

Why it will work.

Trying to convince building owners that energy use reductions are possible in their building is a difficult task using annual energy data and annual energy models when those models do no provide details of their building systems nor can duplicate energy consumption on any day.  The SEE Model can approximately duplicate the real buildings energy consumption on any day providing the owner an opportunity to understand what is being proposed to reduce energy consumption.

Do what?

Periodically, perhaps each day, the city would post on the net the energy use per square foot of varies type buildings at the weather conditions of the previous day and building owners would record energy data of the previous day to compare with the Benchmark data of the previous day. Engineers could propose changes to the owner based on the actual energy use of a building verses the Benchmark Data on the net.

Who will fund this?

Those most likely to set this up in a city would be the Utility Company, a University, Business Organizations, Non-Profit Organizations, or a combination of two or more.

What will it cost?

The cost will be the salary of one engineer located at the city plus a fee for transfer and training of the SEE Model to that engineer. Email Kirby Nelson at kirbynelsonpe@aol.com for details.

City Control

The city could in many ways control the energy conservation program in their city by setting goals for different type buildings and promoting the installation of energy saving concepts.

The following is energy use data for the two system for the weather day given by the figure.

Table 2-90.1-2010 System watts/ft2 on this day

The above charts give SEE Modeled typical metered data for buildings and plants. The top chart is for an all-electric system and the bottom chart is with fuel heat given in watts/ft2 so relative values can be seen. The 24-hour energy use of the 90.1-2010 design is significantly greater than the efficient design, at right. The building energy use consists of the light, plugs, and fans.

Table 4-Efficient Design-watts/ft2 on this day

An office building on this weather day, or similar weather, should if designed to 90.1-2010 consume energy about as shown by the charts at left. The above charts illustrate what is possible with investment in better controls and chiller plant.

Next, we will look at the energy balance of the two designs on this day at this weather.

Table 2 Building & Plant Energy Balance

Energy balance analysis is a powerful tool to understand why and how a building and plant is consuming energy. BTU meters play a very important part in the analysis. If the plant load is measured, then the 14 values that make up the plant load can be challenged. If the SEE Model does not give the plant load as measured then the analysis must adjust, measure, etc., to arrive at a SEE Model plant load that equals the measured plant load. This process can be very revealing as to how the building is responding to the weather conditions of that hour or day.

Table 4 Building & Plant-Energy Balance

Typically, the chiller kW is measured and perhaps the plant kW. If a BTU meter provides the tower exhaust energy, then the energy balance of the plant is easy to define, however plant load BTU metered plus plant kW demand is sufficient.

Comparing these energy balance values to the design values below can be very revealing as to how to improve the systems energy consumption.

Paris France Energy Benchmark Data

Design Day Conditions

The following gives design day performance of the two systems.

A procedure to accomplish two major objectives is presented by utilizing a System Energy Equilibrium (SEE) Model.

- Use the SEE Model to define significant reductions in energy consumption of buildings.

- Generation of business to accomplish the energy use reductions.

How to accomplish these objectives starts with showing building owners, on any given day, that their building is using more energy, if in fact it is, than a ASHRAE Standard designed building, or a building and plant upgraded with new air handler system and plant. Go to the April 2022 ASHRAE Journal newsletter for a description of the (SEE) Model.

To illustrate the concept a SEE Model of a large office building will be modeled at real weather conditions, shown above. This section defines the design conditions of the two designs.

The building is designed with one air handler for each of the 13 floors. The air handler provides cooling for the interior of the building and heating and cooling for the perimeter of the building. The schematics below illustrate the two designs presented here. The Table 2 design is based on ASHRAE Standard 90.1-2010, and the Table 4 design presents a more efficient air control system and a more efficient chiller/tower plant. The SEE Model will define twenty-four-hour energy use for a large office building.

Design Performance

The above figure illustrates the assumed design weather conditions for both designs.

Table 2-90.1-2010 System watts/ft2 on design day

The above charts give typical metered data for buildings and plants. The bottom chart is with fuel heat given in watts/ft2 so relative values can be seen, however at design day conditions HVAC building heat is typically not required. The 24-hour energy use of the 90.1-2010 design is significantly greater than the efficient design at right. The building energy use consists of the light, plugs, and fans.

Table 4-Efficient Design-watts/ft2 on design day

An office building on this design weather day, or similar weather, should if designed to 90.1-2010 consume energy about as shown by the charts at left. The above charts illustrate what is possible with investment in better controls and chiller plant.

Next, we will look at the energy balance of the two designs at design day.

Figure-Table 2 System

The above Figure is the energy balance of the Table 2 (90.1-2010) design and the Figure at right is of the Table 4 design that consists of a more efficient air handler system and chiller/tower plant. The Table 4 design also includes exhaust air energy recovery as shown. However, the building structure and the light and plug levels are the same for both designs. The light level is input at .81 watts/ft2 and the plugs at .74 watts/ft2.

The above energy balance figures are equivalent to the calculations the design engineers would perform during the design of the building and plant. The following schematics define the two designs.

Figure-Table 4 System

Exhaust air recovery

Comparing the energy balance of the two designs illustrates the reduced energy consumption of the Table 4 design.

Schematic-Table 2 Building at Design Conditions

Schematic-Table 2 Plant Design

Schematic-Table 4 Building at Design Conditions

Schematic-Table 4 Plant Design

The above schematics illustrate the level of detail within the SEE Model, detail that is necessary to accurately define the performance of the two systems. The reader is encouraged to review other documents on this site and study the schematics with the understanding that basic HVAC equations define the schematics.

The reader is encouraged to visit the ASHRAE Journal Review post on this site which demonstrates the inadequacies of the annual energy model.

Best regards to all,

Kirby Nelson P.E.

Life Member ASHRAE

NOMENCLATURE

Building structure.

BLD ft2 = air-conditioned space

# Floors = number of building floors

Roof ft2 = roof square feet

N/S wall ft2 =north/south wall square feet

E/W wall ft2 =east/west wall square feet

Wall % glass = percent of each wall that is glass

Glass U = glass heat transfer coefficient

Wall U = wall heat transfer coefficient

Glass SHGC = glass solar heat gain coefficient

Wall emit = wall solar index

Wall weight = #/ft2

Roof weight = #/ft2

Building interior space.

Rooftrans-ton =roof load to interior (ton)

Roofsky-lite-ton =sky lite load (ton)

# people = number people in building

Peopleton sen&lat = sensible & latent cooling load (ton)

Plugton&kW = cooling load & kW due to plug loads

Lightton&kW = cooling load & kW due to lights

Total Bldint-ton = total building interior load (ton)

(cfm) to-per-return = CFM of interior supply air that returns to perimeter of building

Tstat-int = interior stat set temperature (F)

Bldint-air-ton = supply air ton to offset interior load

BLD kW = total building kW demand

FAN kW = total fan kW

Duct Heat kW = kW heating supply air

FA Heat = Fresh air heat

Heat Total = Total building heat

SITE kW = total site kW=Bld+ Fan+Heat

Building perimeter space.

%clear sky = percent clear sky

Tdry bulb = outside dry bulb temperature (F)

Twet bulb = outside wet bulb temperature (F)

Ex/Infillat-ton = latent air infiltration or exfiltration (ton)

Ex/InfilCFM = air infiltration or exfiltration CFM

Exfilsen-ton =sensible air exfiltration or infiltration (ton)

Rooftrans-ton = Roof load to perimeter (ton)

Walln trans ton = north wall transmission (ton)

Walls trans ton = south wall transmission (ton)

WallE trans ton  = east wall transmission (ton)

Wallw trans ton = west wall transmission (ton)

Roof+Walltot-trans-ton = total wall/roof transmission (ton)

GlassN-trans-ton = north wall glass transmission (ton)

GlassS-trans-ton = south wall glass transmission (ton)

GlassE-trans-ton = east wall glass transmission (ton)

GlassW trans-ton = west wall glass transmission (ton)

Glasstot-trans-ton = total transmission thru glass (ton)

GlassN-solar-ton = north glass solar load (ton)

GlassS-solar-ton = south glass solar load (ton)

GlassE-solar-ton = east glass solar load (ton)

GlassW-solar-ton = west glass solar load (ton)

Glasstot-solar-ton = total glass solar load (ton)

Wall heat = Heat provided by window panel (ton)

(int cfm)per-ton = effect of interior CFM to wall (ton)

Total Bldper-sen-ton total perimeter sensible load (ton)

Tstat-per = perimeter stat set temperature (F)

Bldper-air-ton = supply air ton to offset perimeter load

Air handler duct system-Interior duct

Tair supply int = temp air supply to building interior (F)

(fan)int ter ton&kW = interior ton & kW due to terminal fans

(D)int-air-ton = cooling (ton) to building interior duct

Tair coils = supply air temperature off coils to duct (F)

(D)int-CFM = supply air CFM to building interior duct

Perimeter duct

Tair supply per =temp (F) air supply to building perimeter

(fan)per ter ton&kW = perimeter ton & kW of terminal fans

Theat-air = temp supply air before terminal fan heat (F)

(D)heat-ton&kW = heat to perimeter supply air ton & kW

Treheat air = temp perimeter supply air after reheat (F)

(D)reheat ton&kW = reheat of perimeter supply air ton & kW

(D)per-air-ton = cooling (ton) to perimeter duct

Tair coils = supply air temperature off coils to duct (F)

(D)per-CFM = supply air CFM to perimeter duct

Coil

(Coil)sen-ton = sensible load on all coils (ton)

(Coil)L+s-ton = latent + sensible load on all coils (ton)

# Buildings = Number of building loads to plant (ton)

Plant load = Sensible + Latent load to plant

VAV Fan system

Fresh air

CFM\Person = Fresh air cfm/# people in building

Ventilation ACH = Fresh air changes per hour (cfm/ft3)

TOSA-DB-F = OSA DB temp before exhaust air recovery (F)

statFA = fresh air freeze stat set temperature (F)

TFA to VAV = temperature of fresh air to VAV fan

(FA)sen-ton = fresh air sensible load (ton)

(FA)CFM = CFM fresh air to VAV fan inlet

(FA)Lat-ton = fresh air latent load (ton)

(FA)kW = heat kW to statFA set temperature

Air return

TBLD-AR = return air temp (F) before return fans

(Air)ret-CFM = CFM air return from building

(FAN)ret-kW = return fans total kW

(FAN)ret-ton = cooling load (ton) due to (FAN)ret-kW

(Air)ret-sen-ton = return air sen (ton) after return fans

(Air)ret-lat-ton = return air lat. (ton) after return fans

TAR to VAV = TBLD-AR + delta T due to return fans kW

VAVret-sen ton = return sensible (ton) to VAV fans inlet

VAVret-lat ton = return latent (ton) to VAV fans inlet

VAVret-CFM = return CFM to VAV fans inlet

Exhaust air

ExLat-ton = latent load (ton) exhausted

ExCFM = CFM of exhaust air

TEx = temperature of exhaust air

Exsen-ton = sensible load (ton) exhausted

Texh-rec = Air temp after exhaust recovery (F)

% Recovery = % exhaust air energy to fresh air

VAV Fans

Tret+FA = return and fresh air mix temperature (F)

(dh) = VAV air static pressure (in)

Efan-VSD = VAV fans efficiency

VAVinlet-sen-ton = sensible load (ton) inlet to VAV fans

VAVinlet-lat-ton = latent load (ton) inlet to VAV fans

Tair-VAV = temp air to coils after VAV fan heat

(FAN)VAV-CFM = CFM air to coils

(FAN)ton-VAV = load (ton) due to VAV fan kW

(FAN)kW-VAV = total VAV fan kW demand

(FAN)watts/cfm = VAV fans watts/cfm

VAV cfm ACH = VAV cfm air changes per hour

AIR SIDE SYSTEM PLUS BUILDING

Space w/ft2 =People space w/ft2

Fans w/ft2  = total air handlers w/ft2

HEAT w/ft2 = total building heat w/ft2

Building w/ft2 = total building w/ft2

Bld Shell (ton) = total building shell load due to weather

Fresh air (ton) = Sensible + Latent to building (ton)

VAV fans w/cfm = VAV fan power (watts/cfm)

CENTRAL PLANT

# Buildings = number of buildings served by plant

Plant ton = total load (ton) to plant

Primary/secondary pumping nomenclature

gpmevap = total gpm flow thru one evaporator

(H)pri-total = total primary pump head (ft) = (H)pri-pipe + (H)pri-fittings + (H)pri-bp + (H)evap

(H)pri-pipe = primary pump head due to piping (ft)

(H)pri-fittings = primary head due to pump & fitting (ft)

(Ef)c-pump = efficiency of chiller pump

Pc-heat-ton = chiller pump heat to atmosphere (ton)

pumpc-kW = one chiller pump kW demand (kW)

Pchiller-# = number chiller pumps operating

Pumpc-kW = total chiller pump kW

(lwt)evap = temperature water leaving evaporator (F)

Tbp = temperature of water in bypass (F)

gpmbp = gpm water flow in bypass

(H)pri-bp = head if chiller pump flow in bypass (ft)

(ewt)evap = temp water entering evaporator (F)

Psec-heat-ton = secondary pump heat to atmosphere (ton)

Psec-kW = kW demand of secondary pumps

Efdes-sec-p = design efficiency of secondary pumping

Efsec-pump = efficiency of secondary pumping

(H)sec = secondary pump head (ft) = (H)sec-pipe + (H)sec-bp + (H)coil + (H)valve

(H)sec-pipe = secondary pump head due to pipe (ft)

(H)sec-bp = head in bypass if gpmsec > gpmevap

GPMsec = water gpm flow in secondary loop

(ewt)coil = water temperature entering coil (F)

(lwt)coil = temperature of water leaving coil (F)

Evaporator

(evap)ton = load (ton) on one evaporator

TER = evaporator refrigerant temp (F)

TER-app = evaporator refrigerant approach (F)

EVAPton = total evaporator loads (ton)

(H)evap = pump head thru evaporator (ft)

(evap)ft/sec = velocity water flow thru evaporator

(evap)des-ft/sec = evaporator design flow velocity

Compressor:

(chiller)kW = each chiller kW demand

(chiller)lift = (TCR – TER) = chiller lift (F)

(chiller)% = percent chiller motor is loaded

(chiller)# = number chillers operating

(CHILLER)kW = total chillers kW

(chiller)kW/ton = chiller kW per evaporator ton

Plant kW = total kW demand of plant

(Plant)kW/site ton = Plant kW per site ton

Condenser:

(cond)ton = load (ton) on one condenser

TCR = temperature of condenser refrigerant (F)

TCR-app = refrigerant approach temperature (F)

(COND)ton = total load (ton) on all condensers

(H)cond = tower pump head thru condenser (ft)

(cond)ft/sec = tower water flow thru condenser

Tower piping nomenclature

Pipesize-in = tower pipe size (inches)

gpmT = each tower water flow (gpm)

GPMT = total tower water flow (gpm)

(H)T-total = total tower pump head (ft)

PT-heat = pump heat to atmosphere (ton)

pumpT-kW = each tower pump kW demand

EfT-pump = tower pump efficiency

Ptower # = number of tower pumps

PumpT-kW = total tower pump kW

(H)T-pipe = total tower pump head (ft)

(ewt)T = tower entering water temperature (F)

(H)T-static = tower height static head (ft)

Trange = tower range (F)= (ewt)T – (lwt)T

(lwt)T = tower leaving water temperature (F)

Tapproach =  (lwt)T – (Twet-bulb)

Tower nomenclature

tfan-kW = kW demand of one tower fan

Tfan-kW = tower fan kW of fans on

tfan-%  = percent tower fan speed

tton-ex = ton exhaust by one tower

T# = number of towers on

Tton-ex = ton exhaust by all towers on

Trg+app = tower range + approach (F)