ASHRAE Journal Review of June 2022 Article. “Water-Cooled to Water-Cooled Chiller Replacement Saves Big” Hong Kong Queensway Government Offices.

Contents

- Introduction.

- Modeled building and chiller plants defined.

- Performance (watts/ft2) of building and plant. Figs 3-7

- Energy Balance Analysis.          Figs 8-11

- Building Perimeter Model.

Figs 12-21

- Air Handler Model. Fig 22-56

- Chiller Plant Model. Figs 57-75

- Real Weather performance.

For February 21, 2022. Fig 76-80

For June 17, 2022. Fig 81-85.

1-Introduction

The ASHRAE Journal article of June 2022, “Water-Cooled to Water-Cooled Chiller Replacement Saves Big” describes a chiller plant replacement project. The last sentence of the article states, “The ongoing control strategies for better energy efficiency can be further enhanced by real-time monitoring, commissioning and optimization”.

The purpose of this paper is to show that real-time monitoring coupled with a real time System Energy Equilibrium (SEE) Model would add additional enhancement.

The authors of the ASHRAE Journal article demonstrate a wealth of knowledge and experience. Their review and critique of the SEE Model would be of value to the ASHRAE community.

Kirby Nelson P.E.

Life Member ASHRAE

A brief discussion of the SEE Model can be reviewed at the ASHRAE Journal Newsletter of April 12, 2022. The SEE Building Model is driven by a change in weather that results in a new load to the chiller plant. The building model and plant model are two separate models.

## How Buildings, Chiller Plants Work: Discovering the SEE Model

# How Buildings, Chiller Plants Work: Discovering the SEE Model

By Kirby Nelson, P.E., Life Member ASHRAE

Since retiring in 2001, Kirby Nelson, P.E., Life Member ASHRAE, has been creating his own modeling tool. He developed the System Energy Equilibrium (SEE) Model to better understand how buildings and chiller plants work. The tool can be used to design and understand how a building or plant responds to changes in weather, equipment or control, Nelson said.

The SEE Model can also be used for commissioning and for benchmarking the energy consumption of buildings on any given day, providing a method to compare the energy consumption of real buildings to standard designs as weather changes from day to day. The SEE Model is presently configured to model a building and plant designed to ANSI/ASHRAE/IES Standard 90.1-2010, Energy Standard for Buildings Except Low-Rise Residential Buildings. Other standards can be modeled, and any design or control parameter can be changed within the model.

“The SEE Model is a concept, not a finished product,” said Nelson. “It is an approach to modeling buildings and chiller plants based on the same equations used to design a building and plant…If the concept is accepted, I believe it will become a college course, and utility companies or others, will provide benchmark data for cities, and a few engineers will become proficient in running and developing SEE Models.”

Nelson discussed the SEE Model and its attributes with ASHRAE Journal.

What is the SEE Model?
The System Energy Equilibrium (SEE) Model is a set of building equations and chiller plant equations solved simultaneously by Microsoft Excel. The SEE Model obeys the first law of thermodynamics: energy in = energy out + change in internal energy (Ein = Eout + DE). Therefore, the SEE Model gives an energy balance for any hour of the day.

The equations are, for the most part, basic HVAC equations, such as those found in 2021 ASHRAE Handbook–Fundamentals’ Chapter 2, “Thermodynamics and Refrigeration Cycles,” and Principles of Heating Ventilation and Air Conditioning.

Users can change and add equations, but they need to be HVAC engineers, competent in Excel and trained on the SEE Model.

What does the SEE Model do?
The SEE Model defines the hourly energy consumption characteristics of a building on any given 24-hour day as well as the hourly energy consumption characteristics of a chiller plant on any given 24-hour day.

I am not aware of other models and software that can perform these actions. To my knowledge, no other model solves for each hour of a 24-hour day. This gives engineers the opportunity to post on the internet how much energy a building that is compliant with versions of ASHRAE Standard 90.1-2007 or newer compliant building should have used the day before, which also allows them to approach building owners with data and estimates of possible reductions in energy use and cost.

How does it work?
Microsoft Excel is a program that iterates to a steady-state condition after a change in conditions. The SEE Building Model is driven by a change in weather that results in a new load to the chiller plant, and the SEE Chiller Plant Model is driven by a change in load on the plant. The building model and plant model are two separate models.

The SEE Model requires energy in = energy out; therefore, an energy balance of the building and plant results, providing an analysis tool to compare a real building and plant performance on a given hour or day.

Using the Excel SEE Model, users can chart variables and gain an understanding of how the building and plant work and interact. The SEE Model is for 24 hours, so it is much smaller than the annual, 8,760-hour, analysis programs.

The SEE Model can provide charts of any variable of a building or plant. The program models chillers’ condenser and evaporator refrigerant temperatures, a building’s air and water flows and other characteristics, including outside air infiltration. The SEE Model can also provide a schematic of the building and plant for any hour, and the energy balance feature provides a method to understand and troubleshoot a building and plant on any day utilizing real energy use data on a given day.

Why should engineers know about the SEE Model?
The SEE Model gives engineers another tool for designing and analyzing the energy consumption of buildings and chiller plants. Excel is available to all; therefore, engineers can develop their own SEE Models.

The SEE Model is different because it is set up to model the energy performance of a building and chiller plant on any given 24-hour day. It does not model 365 days. Also, the energy balance feature sets it apart from other models.

How can engineers review the SEE Model?
Go to http://kirbynelsonpe.com to review the SEE Model approach to designing, benchmarking and energy balance analysis of buildings and chiller plants.
The SEE Model cannot be accessed over the internet. It must be transferred to others by download or flash drive, and users must be trained to operate the SEE Model.
Contact Kirby at kirbynelsonpe@aol.com with questions and comment.

2-Modeled building and chiller plants defined.

The 90.1-2010 design of a 56-story office building has a peak load of 1782 ton, significantly less than the 2,560-ton suggested by the June 2022 article.  Many changes could be made to bring the plant load up to about this 2,560-ton value. Three changes were made in the building structure. The percent glass wall was increased from 37% to 67% based on the picture of the building in the Journal.  The glass U value was increased from .55 to U=.90 btu/hr-ft2, and the wall #/ft2 was decreased from 80 to 30, resulting in a peak plant load of 2,480-ton, close to the 2,560-ton suggested by the article.   Figure 1 illustrates the 90.1-2010 building design and Figure 2 illustrates the assumed existing building.

The decision to increase the % glass in each wall was made based on the picture in the article. The other two changes were arbitrary. The authors of the article could provide values of the existing building so a more accurate SEE Model can be developed.

The SEE Model must always be input with the detail characteristics of the building being modeled, including the building, lights & plug kW, air handler system, chiller plant and other as may apply.

90.1-2010 Design

Building 56 Story

Building=665,255 Ft-Sq

Building height=728 Ft

Roof = 11,880 Ft-Sq

All walls 37.0% glass

Roof U=.048 Wall U=.090

Glass U=.55 Glass SHGC=.40

Wall 80#/ft2    Roof 40#/ft2

Footprint

South=80 Ft North=80 Ft

Each wall=58,240 Ft-Sq

East=148.49 Ft West=148.49 Ft

Each Wall=108,104 Ft-Sq

Design plant load

Sensible load = 1185 ton

Total load = 1782 ton

Figure 1: 90.1-2010 Building

Existing Building

Building 56 Story

Building=665,255 Ft-Sq

Building height=728 Ft

Roof = 11,880 Ft-Sq

All walls 67.0% glass

Roof U=.048 Wall U=.090

Glass U=.90 Glass SHGC=.40

Wall 30#/ft2    Roof 40#/ft2

Footprint

South=80 Ft North=80 Ft

Each wall=58,240 Ft-Sq

East=148.49 Ft West=148.49 Ft

Each Wall=108,104 Ft-Sq

Design plant load

Sensible load = 1840 ton

Total load = 2480 ton

Figure 2; Assumed Existing building

Table A gives details of the assumed building input to the SEE Model and resulting 2,193.9 kW demand at design conditions. The building is basically assumed to be designed to ASHRAE Standard 90.1-2010 with the modifications to the building structure as defined above; 67% glass wall verses 37% and decreased wall #/ft2. Figures 1 & 2 illustrate the load to the plant is increased from 1782 ton to 2480 ton. The increased building shell load in turn increased the required air handler system CFM which in turn increased the kW demand of the air handling system which increased the load to the plant. Rather minor changes can result in significant changes in building performance.

Detail performance characteristics of the existing building will be covered below but first let’s briefly review the chiller plant designs.

Table A gives the assumed characteristics of the Hong Kong office building and some of the resulting performance of the building. The authors of the ASHRAE Journal article may wish to provide more accurate data which will be input to the SEE Model and this paper updated.

Table A: Assumed Building

Chiller Plants.

Schematic 1: Old chiller plant

As stated by the article the existing chillers had aged to an average 4.4 COP. The chiller SEE Model had to be degraded to 93% ability to convert electrical energy to refrigerant compression plus the evaporator refrigerant approach was increased from 5.2F to 9.36F and the condenser approach from 4.9F to 9.8F.

Schematic 2: New chiller plant

These three degradations in the chillers resulted in at design chiller COP=4.30 and therefore chiller .818 kW/ton as shown in schematic 1. The design day load of 2,480 ton is defined above by Figure 2. The plant is modeled as six chillers of 512-ton capacity.  Nomenclature at the end of this paper will help understand the plant schematics.

3-Performance (watts/ft2) of buildings and plants

Figure 3: Design Day weather

Figure 3 gives the assumed design day weather conditions.

The following watts/ft2 data is typically given by the utility meters on the site and meters on the plant.

Figure 4: Existing building and old plant performance at design day.

Figure 4 gives the watts/ft2 performance of the existing building and the original plant. Plant energy consumption is greater than the building energy consumption.

Figure 5: Existing building-new plant

Figure 5 gives the existing building and the new plant energy consumption. The plant energy consumption is now less than the building.

Figure 6 gives the assumed existing building watts/ft2 performance and the performance of an upgraded building. The upgraded building installs three changes into the existing building model.

Figure 6: Existing building vs. Upgraded building watts/ft2

The lights are decreased from .86 watts/ft2 to .67 watts/ft2. The building is pressurized with exfiltration occurring verses infiltration of the assumed existing building. The air handler system is upgraded to eliminate powered terminal fans and the return fan is eliminated because exfiltration is designed as occurring at the building perimeter wall of each floor. Figure 6 illustrates a significant reduction in watts/ft2 for the upgraded building at design day conditions of Figure 3.

Figure 7: New Plant & Upgraded building

The combination of upgraded building and new chiller plant results in a significant reduction in energy consumption as demonstrated by Figure 7 verses Figure 5. One additional upgrade to consider is the replacement of the windows. If the assumed area and performance of the windows is approximately correct, then significant reduction in energy consumption can be achieved with a new window system that might include the exfiltration feature.

4-Energy Balance Analysis

The SEE Model is set up to model any hour or 24-hour period on any day of weather and operational conditions. The SEE model is built on Microsoft Excel. Excel is oft time dismissed as a spread sheet, an attitude that misses the power of Excel to solve sets of equations simultaneously. The SEE Model is based on basic HVAC equations that engineers use to design building systems and Excel provides the means to solve the equations leading to the possibility of developing real time simulations of a building or plant. Excel also offers the ability to chart any variable over a given 24-hour period, a characteristic that provides important visibility and understanding not given by annual models. The SEE Model can also be structured to provide schematics of the system, as illustrated above, that provides understanding not given by charts. Perhaps the most important feature of the SEE Model on Excel is the ability to provide energy balance charts where energy into the system equals energy out of the system. A btu meter that measures the load to the plant, plus a SEE Model, provides the ability to analyze a building and plant via energy balance analysis. The following will demonstrate.

Figure 8: Energy balance at 4PM

The energy balance is in units of (ton=12,000 btu/ft2).  Figure 8 is the SEE Model energy balance of the assumed building and new plant at 4PM. Top chart is the building, and the bottom chart is the new plant. If a btu meter on the load to the plant is different than the 2,480-ton given by the SEE Model, then one or more of the other values must change in the model to give the btu meter value. Building kW is the total kW of the building so this is likely a measured value. If the measured building kW is different than the SEE Model then the measured value should be input to the model leaving building weather, people, and air exhaust as variables to be changed in the SEE Model to give the metered value of plant load. If the building weather load must be significantly changed to get a SEE Model plant load that equals the metered value, then problems with the building thermal performance needs to be investigated, illustrating a value of the SEE Model.

The bottom chart, new plant energy balance, provides another check on the SEE Model result. First the plant load, determined as discussed above, would be input to the plant model. Very likely the plant kW, converted to ton, is a measured value and therefore also a check on the model. Metered btu data at the towers, in this case ocean exhaust, would be a valuable addition to the system analysis capability for obvious reasons. Figure 8 illustrates a first step in the energy balance analysis and adjustment of the SEE Model to duplicate a real system. The basic idea is, if you adjust the plant load to equal the metered plant load then the other cumulative values of the SEE Model are necessarily correct. Next, we look at more detail analysis.

Figure 9: Building 4PM Energy Balance

Figure 9 is a more detail, 14 variables, building energy balance at 4PM. If adjustments, as discussed above, for Figure 8 were required then they should be made to the varies terms of Figure 9 based on analysis, calculations, and perhaps tests to define just what detail of the building load to the plant needs to be adjusted. This process of energy balance analysis could identify major opportunities for improving the energy performance of the building or could identify significant better performance than expected.

The bottom line is the performance of the building is better understood via energy balance analysis that requires energy into the building equals energy out of the building and metered values greatly assist in establishing the energy use characteristics of the building.

Figure 10: 24 Hour Energy Balance

Figure 10 illustrates the SEE Model capability to provide energy balance data for all 24 hours of the day. The discussion above regarding 4PM could be performed for any hour, therefore providing significantly more understanding about the energy use characteristics of the building.

Figure 11: 24 Hour Totals

Figure 11 gives 24-hour totals. If metered data is taken over a 24-hour period, then the SEE Model can provide data which adds another dimension to the analysis of the building and plant.

The energy consumption of a building and plant is a very complex problem that requires, I believe, a very detail hour by hour analysis tool to achieve understanding of the system and therefore make intelligent decisions of control, operation, and modifications to the building and/or plant. The SEE Model offers that capability.

Next, we will consider details of the building model. The accuracy of the SEE Model in terms of identifying building use characteristics is a function of the number and accuracy of the SEE Model equations. This analysis does not warrant that all or in fact any of these equations are 100% correct nor that this is all the detail necessary in the SEE Model. All equations are subject to change based on better data or characteristics of a given building. The bottom line is that the SEE Model, as presently configured, is judged as good but acknowledges that it can and will be improved with time and attention to the concepts of the SEE Model.

5-Building Perimeter

SEE Model

The following provides detail information about the assumed building, demonstrating the detail of the SEE Model.

First, we will address the perimeter of the building.

Figure 12: Building transmission loads

The top chart gives the building shell transmission values, and the bottom chart gives the glass transmission. The secondary horizontal axis gives the totals for each chart. Glass transmission drives the total.

Figure 13: Top chart glass solar-Bottom chart total shell transmission.

The bottom chart shows that the peak perimeter load due to weather is 899 ton at 4PM, however this does not include load due to infiltration. The next charts demonstrate 14 loads make up the total.

Figure 14: Building shell loads

The top chart includes roof load on the interior of the building, a small load for this building. This value would be significant if the building had a skylight. Building with about 4 floor sometimes have skylights that drive the cooling load. The bottom chart is the building perimeter loads.

Figure 15: 4PM shell loads-Energy Balance

Figure 15 illustrates the glass solar drives the load. During the morning the east solar would be predominate. Each hour has a very different energy balance chart. The weather load to the building is significantly reduced during cloudy days. As seasons change the solar load changes dramatically. The SEE Model solar input is based on the season and the location of the building in the world. Other variables include orientation of the building, shading systems, and shading from adjacent buildings. The SEE Model attempts to input all variables that make up the solar load to the building.

Blue charts are the existing building & gold charts are the upgraded building.

Figure 16: Existing building perimeter controllable loads

Figure 16 gives the loads to the perimeter that are not in the upgraded building design. Infiltration sensible and latent load is modeled in the existing building because infiltration is defined as a load in the 90.1-2010 office building. Infiltration not only results in a load to the space of the building but also is a change in internal energy of the building as a function of infiltration CFM. Energy into the building will not match energy out of the building without this term, (Ein = Eout + chg energy).

The term (inter cfm) per-ton models the transfer of energy from the interior of the building to the perimeter due to the stat set points. This term is zero because the present model assumes the stats are set at the same value. This can be a major value during both summer and winter if the stats are set differently, depending on the path of return air.

Figure 17: Perimeter Sensible loads- Top chart existing building-Bottom chart upgraded building

Figure 17 top chart gives the existing building perimeter loads with infiltration and the bottom chart gives the upgraded building.

Figure 18: Perimeter sensible loads Top chart existing building-Bottom chart upgraded building

Figure 18 sums the building shell loads for the existing building and upgraded building a rather modest drop in load for the upgraded building.

Figure 19: 4PM building loads

Figure 19 is the energy balance for 4PM illustrated the only difference is the outside air infiltration of the existing building.

Figure 20: AHU CFM & air temp.

Figure 20 gives the perimeter air supply CFM and temperature for the two buildings. The supply temperature of the existing building is 56.04F because the air is heated by the powered terminals.  Figure 21 gives the supply air ton to offset the perimeter load ton.

Figure 21: Air supply to offset load

Building Interior Model

Figure 22: Building internal people #, lights & plug kW

Figure 23: Building interior loads-ton

Figure 24: Interior latent loads-ton

Figures 22-25 establish the building interior load. The SEE Model of the air handler system to meet this load is more complex as illustrated by the following figures.

Figure 25: Building Interior loads & air supply to meet loads

As stated, above.

The SEE Model must always be input with the detail characteristics of the building being modeled, including the building, lights & plug kW, air handler system, chiller plant and other as may apply.

The following will demonstrate the detail of the assumed air handler system for this Hong Kong building.

6-Air Handler System

Figure 26: Air supply CFM & temp.

Figure 27: 24-hour kW demand of air handler system

Figure 28: Air handler kW plus space heat kW

Figure 29: Building interior and perimeter load

Figure 30: Building sensible 7 latent loads

Figure 31: VAV Fan Performance

Figure 32: VAV Fan Performance

Figure 33: Buildings air supply & return

Figure 34: VAV Fan Performance

Figure 35: VAV Fan Performance

Figure 36: Sensible load to coils

Figure 37: Sensible load to plant

Figure 38: VAV Fan Performance

Figure 39: Latent load to plant

Figure 40: Latent Loads

Figure 41: Air temperatures & plant sensible + latent load

Figure 42: Perimeter air CFM & temp.

Figure 43: Sensible & latent load to plant

Figure 44: VAV Fan Performance

Figure 45: VAV Fan Performance

Figure 46: Fresh air performance

The upgraded building has exfiltration not infiltration. Therefore, the fresh air into the building is determined by building pressure requirement, resulting in a very high cfm/person during the time when only three people are assumed in the building.

Figure 47: Air changes per hour (ACH)

Figure 48: Fans performance

Figure 49: Fresh Air

Figure 50: VAV CFM & kW demand

This figure illustrates the complexity of simulating the performance of the VAV fan system. Static pressure & fan efficiency must be modeled as a function of several variables that in turn determine the VAV fan kW.

Figure 51: Fan performance

Figure 52: Fan system kW demand including required space heat.

This figure is more complex when heat is required at the perimeter of the building.

Figure 53: Building kW

Figure 54: Plant load & site/building kW

Figure 55: Building 24-hour values

The above charts have demonstrated the detail of the SEE Model as configured to match the building described in the ASHRAE Journal. The equations that define these charts are all changeable based on the characteristics of the building being modeled.

Figure 56: Building 24-hour kW

One objective of the SEE Model is to duplicate the performance, on any day, of a building, in this case a 56-story office building. if the authors of the Journal article provide details the SEE Model will be changed to better data. Next, we address the chiller plants.

7-Chiller Plant Model Details.

The following charts will illustrate the chiller plants, the existing plant and the new plant as described in the ASHRAE Journal of June 2022.

The chiller is a very complex unit, requiring a good model of the evaporator and condenser refrigerant temperatures to define chiller lift and therefore chiller kW demand.

The chiller plant heat is transferred to the ocean thru a heat exchanger. The ocean temperature is assumed as 84F during the summer and a 4F approach heat exchanger for 88F water to the condenser.

Some charts may not show tower as the heat exhaust device, the word should be ocean, not tower.

The old chiller plant charts are dark color, and the new chiller plant charts are green.

Figure 57: Plant load & kW

Figure 58: Plant performance

Figure 59: Primary/Secondary Pumping

Figure 60: P/S pumping (gpm)

Figure 61: Pumping kW

note as stated above some charts will give tower data when the model is of plant heat exhaust to ocean.

Figure 62: Pump kW

Figure 63: Pump kW

Figure 64: Plant kW

Figure 65: Condenser water gpm

Figure 66: Ocean heat exchanger performance

Figure 67: Evaporator Refrigerant Model performance

Figure 68: Condenser Refrigerant Model performance

Figure 69: Chiller performance

Figure 70: Refrigerant Model

Figure 71: Chiller & Plant kW/ton

Figure 72: Chiller & Plant performance

Figure 73: Plant performance

Figure 74: Plant performance

Figure 75: Old plant vs. New plant

The above charts demonstrate the detail equations that make up the SEE Model of the assumed plants based on descriptions in the ASHRAE Journal article of June 2022. The models will be updated if the authors of the ASHRAE Journal article provide details.

8-Real Weather Analysis for February 21, 2022.

Figure 3: Design Day weather

Figure 76: February 21, 2022, weather

February 21, 2022 was a cold day in Hong Kong resulting in very different energy performance of the building, the perimeter of the building must be heated.

Figure 77: Original building & plant

Space + fans plus heat = total building watts/ft2.

Figure 78: Original building & new plant.

The plant 24-hour value decreased from 31.29 watt/ft2 to 21.69 watt/ft2 with the new plant.

Figure 79: Original building vs. upgraded building performance

The upgraded building as defined above by figures 17 thru 56 has a significantly improvement in energy performance.

The upgraded building, in the authors opinion, can be accomplish with available equipment and controls.

Figure 80: Upgraded building & new plant.

The original building with new plant has, on this February 21 day, a total building plus pant value of about 226 watts/ft2. The upgraded building and new plant value for this cold day is about 98 watts/ft2 or less than half the existing building and new plant.

The upgraded building energy consumption could be further reduced by replacing the wall glass with a more efficient glass.

Analysis with energy balance charts for this cold day would provide a good understanding of the energy use characteristics and opportunities for reduction. A more detail analysis for this day will be addressed later.

8-Real Weather Analysis for June 17, 2022

Figure 81: June 17, 2022 weather

Figure 82: Original building & plant

Space + fans plus heat = total building watts/ft2.

Figure 83: Original building & new plant.

With the new plant the 24-hour plant energy consumption decreased from 32.94 watts/ft2 to 24.73 watts/ft2.

Figure 84: Original building vs. upgraded building performance for weather defined by Figure 81

The upgraded building as defined above by figures 17 thru 56 has a significantly improvement in energy performance.

The upgrade building, in the authors opinion, can be accomplish with available equipment and controls.

Figure 85: Upgraded building & new plant

The original building with new plant has, on this June 17, 2022 day, a total building plus pant value of about 54 watts/ft2. The upgraded building and new plant value for this cloudy summer day is about 44 watts/ft2.

The upgraded building energy consumption could be further reduced by replacing the wall glass with a more efficient glass.

Analysis with energy balance charts for this cloudy summer day would provide a good understanding of the energy use characteristics and opportunities for reduction. A more detail analysis for this day will be addressed later.

The analysis of the 56 story Hong Kong office building had to make several assumptions regarding the design of the building. the authors of the ASHRAE Journal article of June 2022 are requested to provide better data so that the SEE Model can be updated.

I would like to coordinate with the authors of the article to define days when the energy use data of the office is recorded, and I can do a SEE Model energy balance analysis. I think that would be beneficial to all. An ASHRAE R&D program might also be possible if the article authors would pursue that.

Stay tuned for more benchmark days.

Kirby Nelson P.E.

Life Member ASHRAE

NOMENCLATURE

Building structure.

BLD ft2 = air-conditioned space

# Floors = number of building floors

Roof ft2 = roof square feet

N/S wall ft2 =north/south wall square feet

E/W wall ft2 =east/west wall square feet

Wall % glass = percent of each wall that is glass

Glass U = glass heat transfer coefficient

Wall U = wall heat transfer coefficient

Glass SHGC = glass solar heat gain coefficient

Wall emit = wall solar index

Wall weight = #/ft2

Roof weight = #/ft2

Building interior space.

Rooftrans-ton =roof load to interior (ton)

Roofsky-lite-ton =sky lite load (ton)

# people = number people in building

Peopleton sen&lat = sensible & latent cooling load (ton)

Plugton&kW = cooling load & kW due to plug loads

Lightton&kW = cooling load & kW due to lights

Total Bldint-ton = total building interior load (ton)

(cfm) to-per-return = CFM of interior supply air that returns to perimeter of building

Tstat-int = interior stat set temperature (F)

Bldint-air-ton = supply air ton to offset interior load

BLD kW = total building kW demand

FAN kW = total fan kW

Duct Heat kW = kW heating supply air

FA Heat = Fresh air heat

Heat Total = Total building heat

SITE kW = total site kW=Bld+ Fan+Heat

Building perimeter space.

%clear sky = percent clear sky

Tdry bulb = outside dry bulb temperature (F)

Twet bulb = outside wet bulb temperature (F)

Ex/Infillat-ton = latent air infiltration or exfiltration (ton)

Ex/InfilCFM = air infiltration or exfiltration CFM

Exfilsen-ton =sensible air exfiltration or infiltration (ton)

Rooftrans-ton = Roof load to perimeter (ton)

Walln trans ton = north wall transmission (ton)

Walls trans ton = south wall transmission (ton)

WallE trans ton  = east wall transmission (ton)

Wallw trans ton = west wall transmission (ton)

Roof+Walltot-trans-ton = total wall/roof transmission (ton)

GlassN-trans-ton = north wall glass transmission (ton)

GlassS-trans-ton = south wall glass transmission (ton)

GlassE-trans-ton = east wall glass transmission (ton)

GlassW trans-ton = west wall glass transmission (ton)

Glasstot-trans-ton = total transmission thru glass (ton)

GlassN-solar-ton = north glass solar load (ton)

GlassS-solar-ton = south glass solar load (ton)

GlassE-solar-ton = east glass solar load (ton)

GlassW-solar-ton = west glass solar load (ton)

Glasstot-solar-ton = total glass solar load (ton)

Wall heat = Heat provided by window panel (ton)

(int cfm)per-ton = effect of interior CFM to wall (ton)

Total Bldper-sen-ton total perimeter sensible load (ton)

Tstat-per = perimeter stat set temperature (F)

Bldper-air-ton = supply air ton to offset perimeter load

Air handler duct system-Interior duct

Tair supply int = temp air supply to building interior (F)

(fan)int ter ton&kW = interior ton & kW due to terminal fans

(D)int-air-ton = cooling (ton) to building interior duct

Tair coils = supply air temperature off coils to duct (F)

(D)int-CFM = supply air CFM to building interior duct

Perimeter duct

Tair supply per =temp (F) air supply to building perimeter

(fan)per ter ton&kW = perimeter ton & kW of terminal fans

Theat-air = temp supply air before terminal fan heat (F)

(D)heat-ton&kW = heat to perimeter supply air ton & kW

Treheat air = temp perimeter supply air after reheat (F)

(D)reheat ton&kW = reheat of perimeter supply air ton & kW

(D)per-air-ton = cooling (ton) to perimeter duct

Tair coils = supply air temperature off coils to duct (F)

(D)per-CFM = supply air CFM to perimeter duct

Coil

(Coil)sen-ton = sensible load on all coils (ton)

(Coil)L+s-ton = latent + sensible load on all coils (ton)

# Buildings = Number of building loads to plant (ton)

Plant load = Sensible + Latent load to plant

VAV Fan system

Fresh air

CFM\Person = Fresh air cfm/# people in building

Ventilation ACH = Fresh air changes per hour (cfm/ft3)

TOSA-DB-F = OSA DB temp before exhaust air recovery (F)

statFA = fresh air freeze stat set temperature (F)

TFA to VAV = temperature of fresh air to VAV fan

(FA)sen-ton = fresh air sensible load (ton)

(FA)CFM = CFM fresh air to VAV fan inlet

(FA)Lat-ton = fresh air latent load (ton)

(FA)kW = heat kW to statFA set temperature

Air return

TBLD-AR = return air temp (F) before return fans

(Air)ret-CFM = CFM air return from building

(FAN)ret-kW = return fans total kW

(FAN)ret-ton = cooling load (ton) due to (FAN)ret-kW

(Air)ret-sen-ton = return air sen (ton) after return fans

(Air)ret-lat-ton = return air lat. (ton) after return fans

TAR to VAV = TBLD-AR + delta T due to return fans kW

VAVret-sen ton = return sensible (ton) to VAV fans inlet

VAVret-lat ton = return latent (ton) to VAV fans inlet

VAVret-CFM = return CFM to VAV fans inlet

Exhaust air

ExLat-ton = latent load (ton) exhausted

ExCFM = CFM of exhaust air

TEx = temperature of exhaust air

Exsen-ton = sensible load (ton) exhausted

Texh-rec = Air temp after exhaust recovery (F)

% Recovery = % exhaust air energy to fresh air

VAV Fans

Tret+FA = return and fresh air mix temperature (F)

(dh) = VAV air static pressure (in)

Efan-VSD = VAV fans efficiency

VAVinlet-sen-ton = sensible load (ton) inlet to VAV fans

VAVinlet-lat-ton = latent load (ton) inlet to VAV fans

Tair-VAV = temp air to coils after VAV fan heat

(FAN)VAV-CFM = CFM air to coils

(FAN)ton-VAV = load (ton) due to VAV fan kW

(FAN)kW-VAV = total VAV fan kW demand

(FAN)watts/cfm = VAV fans watts/cfm

VAV cfm ACH = VAV cfm air changes per hour

AIR SIDE SYSTEM PLUS BUILDING

Space w/ft2 =People space w/ft2

Fans w/ft2  = total air handlers w/ft2

HEAT w/ft2 = total building heat w/ft2

Building w/ft2 = total building w/ft2

Bld Shell (ton) = total building shell load due to weather

Fresh air (ton) = Sensible + Latent to building (ton)

VAV fans w/cfm = VAV fan power (watts/cfm)

CENTRAL PLANT

# Buildings = number of buildings served by plant

Plant ton = total load (ton) to plant

Primary/secondary pumping nomenclature

gpmevap = total gpm flow thru one evaporator

(H)pri-total = total primary pump head (ft) = (H)pri-pipe + (H)pri-fittings + (H)pri-bp + (H)evap

(H)pri-pipe = primary pump head due to piping (ft)

(H)pri-fittings = primary head due to pump & fitting (ft)

(Ef)c-pump = efficiency of chiller pump

Pc-heat-ton = chiller pump heat to atmosphere (ton)

pumpc-kW = one chiller pump kW demand (kW)

Pchiller-# = number chiller pumps operating

Pumpc-kW = total chiller pump kW

(lwt)evap = temperature water leaving evaporator (F)

Tbp = temperature of water in bypass (F)

gpmbp = gpm water flow in bypass

(H)pri-bp = head if chiller pump flow in bypass (ft)

(ewt)evap = temp water entering evaporator (F)

Psec-heat-ton = secondary pump heat to atmosphere (ton)

Psec-kW = kW demand of secondary pumps

Efdes-sec-p = design efficiency of secondary pumping

Efsec-pump = efficiency of secondary pumping

(H)sec = secondary pump head (ft) = (H)sec-pipe + (H)sec-bp + (H)coil + (H)valve

(H)sec-pipe = secondary pump head due to pipe (ft)

(H)sec-bp = head in bypass if gpmsec > gpmevap

GPMsec = water gpm flow in secondary loop

(ewt)coil = water temperature entering coil (F)

(lwt)coil = temperature of water leaving coil (F)

Evaporator

(evap)ton = load (ton) on one evaporator

TER = evaporator refrigerant temp (F)

TER-app = evaporator refrigerant approach (F)

EVAPton = total evaporator loads (ton)

(H)evap = pump head thru evaporator (ft)

(evap)ft/sec = velocity water flow thru evaporator

(evap)des-ft/sec = evaporator design flow velocity

Compressor:

(chiller)kW = each chiller kW demand

(chiller)lift = (TCR – TER) = chiller lift (F)

(chiller)% = percent chiller motor is loaded

(chiller)# = number chillers operating

(CHILLER)kW = total chillers kW

(chiller)kW/ton = chiller kW per evaporator ton

Plant kW = total kW demand of plant

(Plant)kW/site ton = Plant kW per site ton

Condenser:

(cond)ton = load (ton) on one condenser

TCR = temperature of condenser refrigerant (F)

TCR-app = refrigerant approach temperature (F)

(COND)ton = total load (ton) on all condensers

(H)cond = tower pump head thru condenser (ft)

(cond)ft/sec = tower water flow thru condenser

Tower piping nomenclature

Pipesize-in = tower pipe size (inches)

gpmT = each tower water flow (gpm)

GPMT = total tower water flow (gpm)

(H)T-total = total tower pump head (ft)

PT-heat = pump heat to atmosphere (ton)

pumpT-kW = each tower pump kW demand

EfT-pump = tower pump efficiency

Ptower # = number of tower pumps

PumpT-kW = total tower pump kW

(H)T-pipe = total tower pump head (ft)

(ewt)T = tower entering water temperature (F)

(H)T-static = tower height static head (ft)

Trange = tower range (F)= (ewt)T – (lwt)T

(lwt)T = tower leaving water temperature (F)

Tapproach =  (lwt)T – (Twet-bulb)

Tower nomenclature

tfan-kW = kW demand of one tower fan

Tfan-kW = tower fan kW of fans on

tfan-%  = percent tower fan speed

tton-ex = ton exhaust by one tower

T# = number of towers on

Tton-ex = ton exhaust by all towers on

Trg+app = tower range + approach (F)